SHORT CIRCUIT CURRENT CALCULATION FOR CONDUCTOR AS PER IEC 60949

| Cable Size : 132kV, 1C x 3000mm² | Copper | Conductor |
| --- | --- | --- |

Voltage Grade (kV) = 132 kV

Conductor Cross Sectional Area (sqmm) = 3000 mm²

Conductor material = Copper

Insulation material = XLPE

Type of Outer Sheath = PE

Required SCC rating through Conductor = 40 kA

Duration of short circuit (t) = 1 Second

Note: As per IEC 60949, only adiabatic method is used to calculate short circuit current as, for the conductors with the ratio of short-circuit duration to conductor cross-sectional area less than 0.1 s/mm², the improvement in short circuit current is negligible.

1. Calculation of adiabatic short-circuit current as per Clause No. 3 of IEC 60949

I²ₐᴅt = K²S² ln((θf + β)/(θi + β))     [Eq. 1]

Where;

t  Duration of short circuit (Sec.) = 1 sec

S  Geometrical Cross sectional area of current carrying component = 3000 mm²

θi  Initial Temperature = 90 °C

θf  Final Temperature = 250 °C

β  Reciprocal of temperature coefficient of resistance - Copper (As per Table I of IEC 60949) = 234.5 K

K  Constant depending upon the material - Copper (As per Table I of IEC 60949) = 226 A¹/²/mm²

As per above Eq. 1

IAD  Short circuit current calculated on adiabatic basis = 45.2 kA for 1 second

Calculation Results:

Required cross-sectional area S: 2850 mm²

Maximum current carrying capacity for calculated area:  kA

2. Conclusion

From the calculation above, we can observe that short circuit rating of power cable on adiabatic basis meets the requirement, 40 kA for 1 second.