SHORT CIRCUIT CURRENT CALCULATION FOR THE ALUMINIUM SHEATH AS PER IEC 60949

| Cable Size : 132kV, 1C x 3000mm² | Copper | Conductor |
| --- | --- | --- |

Voltage Grade (kV) = 132 kV

Conductor Cross Sectional Area (sqmm) = 3000 mm²

Conductor material = Copper

Sheath material = Aluminium

Insulation material = XLPE

Type of Outer Sheath = PE

Calculation of Sheath Cross Section area (S)

Thickness of Aluminium Sheath (Min.), t (δ) = 1.7 mm

Diameter before Al sheath, d1 = 93.64 mm

Diameter after Al sheath, d2 = 97.04 mm

Geometrical cross sectional area of Sheath = 495.8 mm²

Required SCC rating through Conductor = 40 kA

Duration of short circuit (t) = 1 Second

1. Calculation of adiabatic short-circuit current as per Clause No. 3 of IEC 60949

I²ₐᴅt = K²S² ln((θf + β)/(θi + β))     [Eq. 1]

Where;

t  Duration of short circuit (Sec.) = 1 sec

S  Geometrical cross sectional area of current carrying component = 495.8 mm²

θi  Initial Temperature = 80 °C

Note: Sheath initial temperature is considered assuming conductor temperature as 90.0 °C

θf  Final Temperature = 250 °C

β  Reciprocal of temperature coefficient - Sheath material-Aluminium (As per Table I of IEC 60949) = 228 K

K  Constant depending upon the material - Sheath material-Aluminium (As per Table I of IEC 60949) = 148 A¹/²/mm²

SHORT CIRCUIT CURRENT CALCULATION FOR THE ALUMINIUM SHEATH AS PER IEC 60949

As per above Eq. 1

IAD  Short circuit current calculated on adiabatic basis = 18.5 kA for 1 second

2. Calculation of non-adiabatic short-circuit current as per Clause No. 2 of IEC 60949

I = ε × Iₐᴅ     [Eq. 2]

Where;

ε Factor to allow for heat loss into adjacent component.

ε = 1 + 0.61M√t - 0.069(M√t)² + 0.0043(M√t)³     [Eq. 3]

M = [√(σ₂/ρ₂) + √(σ₃/ρ₃)] / (2σ₁δ × 10⁻³F)     [Eq. 4]

σ₂ Volumetric specific heat of media below the sheath (Table II of IEC 60949) = 2400000 J/K.m³

σ₃ Volumetric specific heat of media above the sheath (Table II of IEC 60949) = 2400000 J/K.m³

σ₁ Volumetric specific heat of sheath (Table I of IEC 60949) = 2500000 J/K.m³

ρ₂ Thermal resistivity of media below the sheath (Table II of IEC 60949) = 3.5 K.m/W

ρ₃ Thermal resistivity of media above the sheath (Table II of IEC 60949) = 3.5 K.m/W

δ Thickness of metallic sheath = 1.7 mm

F Factor to account for imperfect thermal contact = 0.7

Note: It is recommended that a value of F=0.7 be used except that when the metallic component is completely bonded on one side to the adjacent medium, a value of F=0.9 can be used.

As per above Eq. 4

The factor M = 0.85

As per above Eq. 3

The factor ε = 1.125

Iₐᴅ Short circuit current calculated on adiabatic basis = 18.5 kA for 1 second

I Short circuit current calculated on non adiabatic basis = 20.8 kA for 1 second

3. Conclusion

From the calculation above, we can observe that short circuit rating of Aluminium sheath of power cable meets the requirement, 40 kA for 1 second